

**US Army Corps of Engineers**

**Afghanistan Engineer District**

AED Design Requirements: Package Waste Water Treatment Plants and Lagoons

(Provisional)

Various Locations, Afghanistan

September 2009 Version 1.2

**TABLE OF CONTENTS**

AED DESIGN REQUIREMENTS FOR

PACKAGE PLANT VARIOUS LOCATIONS, AFGHANISTAN

Section Page

**1. General 1**

**2. Package Plant 1**

**3. Site Selection 2**

**4. Treatment Requirements 2**

**5. Basic Design Considerations 4**

**6. Selection of Treatment Process 5**

**7. Lagoon Treatment Systems 8**

**8. System Submittals 11**

**9. As-Builts 14**

**10. References 14**

Tables

Table 1. Information on Materials Which Inhibit Biological Treatment Processes 3

Table 2. Capacity Factors 4

Table 3. Per Capita Sewage Flows 5

Table 4. Assumed Wastewater Influent Characteristics Flows 5

Table 5. Description of Activated Sludge Processes for Use at Medium-Size Installations 7

Table 6. Types of Design and Operational Issues at Package WWTP 8

Table 7. Description of Lagoon Treatment Systems for Use at Medium-Size Installations 9

|  |  |
| --- | --- |
| Table 8. Area BOD5 Design Loading of Facultative Lagoon Treatment Systems | 9 |
| Table 9. Partial-Mix Aerated Lagoon Treatment Systems | 10 |
| Table 10. Assumed Partial-Mix Aerated Lagoon Aeration Requirements | 11 |
| Table 11. Summary of WWTP Design Parameters to be Included in Submittal | 13 |
| Figure  Figure 1 Classification Sketch of Activated Sludge Variations | 6 |
| Appendices  Appendix A Outside Design Climate Conditions | 15 |
| Appendix B Solubility of Oxygen in Fresh Water | 16 |
| Appendix C Determination of Equalization Storage for Package WWTP | 17 |
| Appendix D Summary of Markup Pages for UFGS 44 41 13 | 18 |

**1. General**

The purpose of this document is to provide wastewater treatment plant (WWTP) design requirements to Contractors for projects at medium-sized installations. It is a summary of requirements that should be provided in design submittals. References contained herein provide more specific design procedures and examples. Medium-sized installations are considered those requiring the design and construction of package plant for wastewater treatment for average daily waste water flow rates of between 60 cubic meter/day (15,000 gpd) and 378 cubic meter/day (100,000 gpd). Projects at small- sized installation with projected wastewater flows smaller than this range should be evaluated for onsite treatment systems such as septic/leach field disposal or self-contained lagoon systems. Septic and leach field systems are discussed in the USACE-AED Design Requirements Sanitary Sewer and Septic Tank System, 2009.

The contractor's design and construction shall comply with technical requirements contained herein. WWTP design involves several engineering disciplines including civil, mechanical, electrical and structural engineering. The designer shall have a minimum of 5 years experience with the design and construction of pre-engineered package wastewater treatment plants of the same magnitude and complexity as required in this project. The designer shall be responsible for providing (as demonstrated in shop submittals, Section 8) project experience in all the specialized disciplines and possess knowledge of the construction of package wastewater treatment plants as well as construction and industry standards for wastewater treatment plants.

**2. Package Waste Water Plant**

Treatment systems handling less than 378 cubic meters per day (100,000 gpd) are generally considered small package WWTP systems. For some packaged treatment systems, the principles of design are no different than larger plants with customized design but the choice of equipment will usually differ from that used in large plants. In addition, the level of redundancy for process components, and the types of containment systems may be dramatically different because package systems are pre-engineered and components may be constructed offsite. Packaged WWTPs must use larger safety factors for flow variation, altitude and temperature effects relative to total wastewater flows, and the lack of daily maintenance. Package WWTPs inherently have less operational flexibility; however, they are nonetheless capable of performing effectively and economically. Complete WWTPs can be obtained from various manufacturers. Some prefabricated plants may be capable of being relocated, depending on size and original construction. Most of these units are factory fabricated and shipped as complete units, ready for connections to piping and power. Small physical-chemical units have been developed as “add on" units to existing facilities to provide additional treatment efficiency. Shop submittals of package WWTP systems are a contract requirement.

Package plants are appropriate for forward operating bases (FOB) or small permanent installations such as ANP or ANA garrisons. These systems are designed to generally treat between 57,000 L/d (15,000 gpd) and 378,500 L/d (100,000 gpd), however larger capacities can be considered on a case by case basis. For MILCON projects beyond this flow range, the treatment processes used in the package WWTP may require HQDA (CEEC-EB) approval for Army projects and HQ USAF/LEEE approval for Air Force projects, with complete documentation and information to support the requested waiver. The wastewater treatment plant should be designed to achieve effluent quality standards as set forth in reference 1, unless superseded by subsequent host nation environmental guidance. In addition, the plant must be capable of being operated by few (no more than three) operating personnel, capable of being by-passed during operational failures, need a minimum of energy to provide treatment such that the plant can operate using standby power generation for a period of 48-hours. If the package plant design is supplementing the capacity of existing plants, criteria contained herein regarding flows and wastewater characteristics may be modified to conform to existing plant performance data provided the plant has been in operation long enough to have

established that it is meeting effluent quality standards.

**3. Site Selection**

The major factors in the selection of suitable sites for treatment facilities include the following:

• Topography

• Availability of a suitable effluent discharge point

• Access to the plant for construction, operation, and maintenance

• Availability and acceptable location of sludge drying and disposal facilities

• Minimum separation distance between the wastewater plant and living quarters, dining facilities, and water wells of 30 meters

• Site locations shall be selected such that the WWTP is fully operational and functional during a 25-year flood.

The siting criteria for the package plant should consider protection requirements for drinking water sources. Sufficient space must be allocated not only for suitable arrangement of the initial units and associated plant piping but also to accommodate future expansion. The site will be selected so that an all-weather road is available or can be provided for access to the plant.

**4. Treatment Requirements**


Package WWTP for USACE-AED projects will generally be designed to provide secondary treatment consistent with the effluent quality requirements in reference 1. However other levels of treatment may be required depending upon the characteristics of the waste water. *Preliminary* treatment is defined as any physical or chemical process at the wastewater treatment plant that precedes primary treatment. Its function is mainly to protect subsequent treatment units and to minimize operational problems. *Primary* treatment is defined as physical or, at times, chemical treatment for the removal of settleable and floatable materials. *Secondary* wastewater treatment is defined as processes which use biological and, at times, chemical treatment to accomplish substantial removal of dissolved organics and colloidal materials that degrade receiving water and impair its use for other beneficial purposes. Disinfection of waste water to inactivate harmful microorganisms is considered a process that can be used in conjunction with both primary and secondary treatment processes. *Advanced* wastewater treatment is defined as that required to achieve pollutant reductions by methods other than those used in secondary and primary treatment (sedimentation, activated sludge, trickling filter, etc.). Before treatment plant design is begun, treatment requirements will be determined on the basis of meeting stream and effluent requirements.

Pretreatment of pollutants which may interfere with operation of a sewage treatment plant or pass through such a plant untreated may be required. Additionally, in many cases, pretreatment of industrial or maintenance facilities wastewater such as laundry waste water and water desalination treatment plant brine and back wash will be necessary to prevent adverse effects on the sewage treatment plant processes. Some types of industrial waste may be admitted to wastewater treatment plants, e.g., cooling tower discharges, boiler blowdown, vehicle washrack wastewater, swimming pool filter discharges, and aircraft wash wastes using biodegradable detergents. Flow of industrial wastewater may be reduced through process modification or wastewater recirculation. Adverse impacts on the treatment plant can be mitigated by reducing the concentration of those compounds such as bleach or disinfectants causing the problem. Table 1 is a listing of compounds which inhibit

biological treatment processes. In some cases, the adverse impact may be caused by short-lived occurrences of either wastewater containing high concentrations of compounds or a wastewater flow rate much higher than the average daily flow. This situation, which is commonly called “slugs,” may, in some cases, be managed by including an equalization basin upstream of the treatment plant.

Advanced treatment employs a number of different unit operations, including ponds, post-aeration, microstraining, filtration, carbon adsorption, membrane solids separation, and specific treatment processes such as phosphorus and nitrogen removal. Advanced wastewater treatment is capable of very high effectiveness and is used when necessary to meet strict effluent standards. Organics and suspended solids removal of over 90 percent is obtainable using various combinations of conventional and advanced wastewater treatment processes. Phosphorus levels of less than 1 milligram per liter and total nitrogen levels of 5.0 milligrams per liter or less can also be reached through advanced treatment.


**Table 1. Materials Which Inhibit Biological Treatment Processes**



**5. Basic Design Considerations**

The required treatment processes are determined by the influent characteristics, the effluent requirements, and the treatment processes that produce an acceptable effluent. Influent characteristics are best determined by laboratory testing of samples from an existing waste stream or from a similar waste stream; but they may be predicted on the basis of standard waste streams as stated in the contract technical requirements. Treatment capacity is based on the design population, effective multiplied by a Capacity Factor) which is a projected population obtained by analysis, per capita loading rates and other industrial or operational waste water loads. The effective population and per capita loading rates are given for each project in the contract technical requirements. The design population is determined by adding the total resident and 1/3 the non-resident populations and multiplying by the appropriate capacity factor taken from table 2 which allows for variations in the using population.

**Table 2. Capacity Factors**



The rates of sewage flow vary widely throughout the day. The design of process elements in a sewage treatment plant is based on the average daily flow. Transmission elements, such as conduits, siphons and distributor mechanisms, will be designed on the basis of an expected peak flow rate of two times the average rate or the peak hourly rate for a specific process or conveyance component given in Reference 3. For example secondary clarifiers will be designed for a peak hourly flow rate (i.e., 1.75 times the average daily rate). Consideration of the minimum rate of flow is necessary in the design of certain elements, such as grit chambers, measuring devices and dosing equipment; for this purpose, 40 percent of the average flow rate will be used. The average daily wastewater flow to be used in the design of new treatment plants will be computed by multiplying the design population by the per capita rates of flow. Unless already provided in the contract technical requirements, per capita wastewater flows can be determined from Table 3, and then adjusting for such factors as industrial wastewater flow and infiltration. Where shift personnel are engaged, the flow will be computed for the shift when most of the people are working. A check on sewage volumes could be to compare water consumption to the sewage estimate (neglecting infiltration, which will be considered subsequently). About 60 to 80 percent of the consumed water will reappear as sewage, the other 20-

40 percent being lost to irrigation, wash-down, and points of use not connected to the sewer. If existing flow data are not available the wastewater flow fraction of water use shall be considered 80 percent.

**Table 3. Per Capita Sewage Flows (1)**

|  |  |
| --- | --- |
| **Installation** | **Per capita, liters/day (gal/day) (2)** |
| U.S. bases | 152 (40) |
| ANA/ANP and other host nation | 125 (33) |

Notes:

(1) Wastewater per capita rates in contract technical requirements shall take precedence over these values

(2) AED per capita sewage flows are defined as 80% of the per capita water allowance. For example the ANP and ANA per capita water allowance is 155 lpcd (41 gpcd). 80% of this number is reflected in Table 3 above as the per capita sewage flow.

If an existing wastewater stream exists at the project site, the wastewater at existing facilities will be analyzed to determine the characteristics and constituents as required. Analytical methods will be as given in Reference 2. For treatment facilities at new installations which will not generate any unusual waste, the characteristics shall shown in Table 4 unless specifically stated otherwise in the contract technical requirements or as determine by influent sampling and testing using Standard Methods (Reference 2).

**Table 4. Assumed Wastewater Influent Characteristics Flows**

|  |  |
| --- | --- |
| **Parameter** | **Concentration, mg/l unless noted** |
| pH | 7 to 7.5 (standard units) |
| temperature | 20 to 22 degrees celsius |
| BOD5 | 4001 |
| Total suspended solids | 400 |
| Total nitrogen | 80 |
| Ammonia nitrogen | 15 |
| Oils and grease | 100 |
| Phosphorous | 15 |
| Chloride | 100 |
| Hardness | 200 |

Notes: BOD5 shall be the greater number based on 400 mg/l or based on 0.09 kg/capita-day (0.2 lb/capita-day)

Concentrations are presented above in milligrams per liter; which is equivalent to parts per million (ppm). These values represent an average waste and therefore should be used only where detailed analysis is not available. When the water supply analysis for the installation is known, the above analysis will be modified to reflect the normal changes to constituents in water as it arrives at the wastewater treatment plant. Industrial waste loadings can also be characterized to a large extent by normal sewage parameters. However; industrial waste contains contaminants not generally found in domestic sewage and is more variable than domestic sewage in terms of pH, biochemical oxygen demand, chemical oxygen demand, oil and grease, and suspended solids. Each industrial wastewater must be characterized individually to determine any and all effects of treatment processes.

**6. Selection of Treatment Process**

Packaged WWTPs combine the different levels of treatment described in the previous section into a single treatment train. The secondary treatment process in the treatment train may consist of trickling filter plants, rotating biological discs, membrane bioreactors, physical-chemical technology, or an aerobic suspended growth (activated sludge) biological treatment process. Physical-chemical systems also have the flexibility to operate in an on-off mode which is not possible with biological systems. However, they are often costly to operate, require skilled attention, and produce large

require training of Afghan nationals for the operation and maintenance in remote locations. Membrane bioreactors (MBR) which are now common in the U.S. at small package WWTP installations, use low pressure micro or ultra filtration membranes and eliminate the need for secondary clarification and filtration. The membranes are usually suspended in an aerated tank. The main advantage of MBRs is that they overcome the poor settling of sludge that can occur in convention activated sludge processes.

Pre-engineered package WWTP’s used at USACE-AED projects are predominantly aerobic suspended growth (activated sludge) biological treatment processes. Although many variations of the activated sludge process exist, the three which have been most successful for USACE-AED projects are extended aeration, sequencing batch reactor and contact stabilization plants. Figure 1 lists processes applicable to USACE-AED projects including the three named previously.

**Figure 1 Classification Sketch of Activated Sludge Variations**

**Aerobic suspended-growth processes**

Activated sludge process *Activated sludge process* for large installations *for small installations* (greater than 378 cu m/day) *(60 to 378 cu m/day)*

Activated sludge process for nutrient removal (oxidation, nitrification & denitrification)

*extended sequencing contact aeration batch stabilization*

*variations reactor tanks*

Large WWTPs for installations that anticipate average daily flow greater than 378 cubic meter/day (100,000 gpd) are better suited to complete mix or plug flow activated sludge processes that are only considered to be subsets of the activated sludge process on the left side of the above figure.

Table 5 describes the differences between the three types of activated sludge processes highlighted in Figure 1. Note variations of other activated sludge process may be selected for pre-engineered wastewater package plants but the highlighted variations have already been approved and provided successful operation at USACE-AED projects.

**Table 5. Description of Activated Sludge Processes for Use at Medium-Size Installations**

|  |  |
| --- | --- |
| **Process** | **Description** |
| Extended aeration | A plug flow process that operates for a relatively longer aeration time at lower loading rates resulting in  the biochemical degradation of the organic matter as well as d the heterotrophic bacteria in the reaction. Hydraulic residence times are typically 18 to 36 hours and biological loading rates are 64 to 190 kg  BOD /m3-day (5 to 15 lb BOD / 103- ft3-day).  5 5 |
| Sequencing batch reactor | A fill and draw type biological reactor involving one or two complete mix reactors in which all the steps of the  activated sludge process occurs. A separate secondary sedimentation tank is not required, but typically two reactors are required for sequencing. Hydraulic residence times are typically 12 to 50 hours and biological loading rates are 64 to 190 kg  BOD /m3-day (5 to 15 lb BOD / 103- ft3-day).  5 5 |
| Contact stabilization | Two tanks or compartments are used to mix the  influent with the activated sludge; during treatment, the mixed liquid is settled in a secondary settling tank and return sludge is aerated in a separate reaeration basin to stabilize organic matter. Hydraulic residence times are typically 4 to 8 hours and biological loading  rates are 765 to 950 kg BOD /m3-day (60 to 75 lb  5  BOD / 103- ft3-day).  5 |

Design procedures for these processes are contained in references 4 and 5. The designer shall consider the affect of high temperature and elevation at the project in the calculation of aeration requirement for secondary treatment and accordingly size the air diffusers blowers or mechanical mixers with adequate size motors for the project site conditions.

A typical system consists of the following components.

• Influent manhole that receives and conveys raw wastewater flows to a lift station or headwork where there the wastewater receives comminution and hydraulic energy potential needed to transport the flow through the entire plant (except as provided by recirculation pumps)

• Headwork to provide coarse screening, primary sedimentation and flow measurement

• Flow equalization to store peak flows and recycled activated sludge

• Aeration basin with air diffusers or mechanical aerators with return activated sludge pump capability

• Secondary sedimentation including waste sludge collection and pumping to sludge drying facility

• Sludge drying beds

• Chorine contact chamber for effluent disinfection

• Effluent gravity or pumping system to convey the effluent flow to the proposed outfall location at the receiving surface water point

• Emergency bypass pipe and valve system

Package WWTP systems need to provide safety factors such as equalization basins, generous loading capacity and aeration capacity, and emergency bypass provisions because they do not have the parallel trains required in Reference 3 for permanent WWTP facilities. Parallel components may be required depending upon the size of the package WWTP and the safety factors used in design.

The basis of design for the package WWTP shall be completely documented using the submittal process. Submittal can be through the project design submittal process or using ENG FORM 4025, Transmittal of Shop Drawings, Equipment Data, Material, Samples, or Manufacturer’s Certificates of Compliance, however 100% final design submittal shall include all submittal information to provide a single set of documents for future reference. Section 8 describes the submittal requirements.

The major design and operational issues that affect package plants are summarized in Table 6. The design shall provide explanations of how these issues will be mitigated by the proposed system.

**Table 6. Types of Design and Operational Issues at Package WWTP**

|  |  |
| --- | --- |
| **Issue** | **Discussion** |
| Hydraulic shock loads | Provide equalization tank |
| Large fluctuations in BOD loading | Provide equalization tank and pump equipment  necessary for recirculation |
| Small flows that are do not self clean conduits  and channels | Provide adequate water service to allow washing  channels and lift stations |
| Positive sludge return provisions that allow an  extended aeration system to meet all normal requirements | Pump capacity for recirculation ratio of up to 3:1 |
| Adequate provisions for scum or froth and grease removal from the secondary clarifier | Provide scum collection facilities and pumping equipment to return the scum and froth to the  equalization tank |
| Denitrification in final clarifier that results in solids  discharge in the effluent | Overflow rates limited to 24 to 33 m3/m2 – day  600 to 800 gal/ft2 – day |
| Adequate removal and storage of waste sludge | Provide holding tank for sludge storage (may be  combined with equalization) |
| Provision to adjust to large and rapid temperature  changes | Size aeration facilities for expected high  temperature at project site using site climatic data given in mechanical section of RFP technical requirements |
| Adequate air supply rate | Adjust air supply rate for altitude and temperature  extremes anticipated at project site using site climatic data given in mechanical section of RFP technical requirements |

The performance of most package WWTPs can be improved by sizing facilities with using conservative design parameters and providing sufficient storage for handling side stream flows.

**7. Lagoon Treatment Systems**

Lagoon wastewater systems are earthen basins that are engineered for BOD and total suspended solids removal similar to package WWTPs; however, they are sized such that the biological loading rate is lower than traditional aerobic suspended growth processes such as in pre-engineered package WWTP plants. In addition BOD is removed by sedimentation. These systems are capable of providing effluent quality that meets the technical requirements, however, they are affected by climate conditions and shock loading and require conservative design factors. They provide significant removal of pathogens as a result of natural die-off, sedimentation, and adsorption.

The design requirements include embankment design, impermeable layer or liner design, erosion control design both for the embankment and outlet features, and hydraulic design for pipe lines and lift stations (if needed). These design requirements are considered in other design guides and Unified Facility Criteria (UFC). The information presented in this section demonstrates the type of design information required for project submittal of WWTPs involving lagoons. The information may need to be expanded or adapted for the specific project site.

Two types of lagoons are applicable to USACE-AED projects that are described in Table 7.

**Table 7. Description of Lagoon Treatment Systems for Use at Medium-Size Installations**

|  |  |
| --- | --- |
| **Type of lagoon** | **Description** |
| Facultative | The surface zone is aerobic as a result of wind  shear mixing, but the subsurface zone may be anaerobic or even anoxic. Hydraulic residence times are typically 25 to 180 days and biological  loading rates are 64 to 190 kg BOD5/cu m-day (20 to  60 lb BOD5 / ac-day). Hydraulic depths are typically  1.5 to 2 meters. |
| Aerated Partial-Mix | Surface aeration using mechanical equipment  produces a surface aerobic zone that ranges in depth depending upon the amount and efficiency of oxygen transferred and the lagoon depth Hydraulic residence times are typically 5 to 20 days and biological loading rates are 64 to 190 kg BOD5/cu m-  day (5 to 15 lb BOD / 103- ft3-day). Hydraulic  5  depths are typically 3 to 5 meters. |

The principal advantage of aerated lagoons is that they require less land area and because they are smaller they may be more economical considering lining and covers. They are more expensive to construct and operate and maintain, and the construction of liners that do not fail and are capable of enduring the weight of maintenance vehicles requires more experience. Liner design is a specialized engineering topic and not discussed in this design guide.

The principle design concept for facultative lagoons is to provide sufficient detention time and low organic loading that the surface layer of the lagoon remains aerobic. However these lagoons are subject to wind mixing and thermal turnover at times of the year that can create odors.

Pretreatment of influent for lagoons shall be designed to minimize floatables, scum, and large objects from being transported in to the lagoons. Bar screens are used in combination with primary sedimentation to remove rags, large objects and grit.

Design procedures for facultative lagoons shall be based on area biological loading rates shown in

Table 8.

**Table 8. Area BOD5 Design Loading of Facultative Lagoon Treatment Systems**

|  |  |  |
| --- | --- | --- |
| **Average winter temperature, o C** | **Kg/ha-day** | **Lb/ac-day** |
| Greater than 15 | 45-90 | 40-80 |
| 0-15 | 22-45 | 20-40 |
| Less than 0 | 11-22 | 10-20 |

Notes: Source – reference 6

Design procedures for aerated partial mix lagoons shall be based on hydraulic detention times shown calculated using the following equation:

t= (n/k)\*((Co/Cn)^(1/n)-1)) Eq. 1 where t= hydraulic detention time, days

n= number of equal sized cells

k= BOD removal constant rate, per day

Co= influent BOD concentration to first cell in series, mg/l

Cn= effluent BOD concentration from cell n, mg/l

The BOD removal rate used in 0.276 day-1 based on reference 7. The rate constant is adjusted for the design temperature using the following equation:

k2/k20=theta^(T2-T20) Eq. 2 where k2= BOD removal rate constant at T2

k20= BOD removal rate constant at T20 o

T20= 20 C

o

T2= average winter temperature C

The lagoon area is calculated as the design flow multiplied by the hydraulic detention time divided by the hydraulic depth of the lagoons. In the example below, average winter temperatures were used in equation (2) to compute hydraulic detention times from equation (1) to size three lagoon systems, each containing “n” lagoons in sequence, in 3 locations at 4 different design flow rates. In every case the lagoon hydraulic depth is 3 meters. Results are provided in Table 9. The table shows the size for each lagoon for the number of cells shown in the left column.

**Table 9. Partial-Mix Aerated Lagoon Treatment Systems**

|  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | DESIGN FLOW RATE, cubic meters/day | | | | |  |  |  |  |
|  |  | **61** |  |  | **120** |  |  | **340** |  |  | **680** |  |
|  | Lagoon size, hectare | | | Lagoon size, hectare | | | Lagoon size, hectare | | | Lagoon size, hectare | | |
| **number of cells, n** | Kandahar | Kunduz | Kabul | Kandahar | Kunduz | Kabul | Kandahar | Kunduz | Kabul | Kandahar | Kunduz | Kabul |
| **1** | 0.30 | 0.28 | 0.38 | 0.60 | 0.56 | 0.74 | 1.70 | 1.58 | 2.10 | 3.40 | 3.17 | 4.20 |
| **2** | 0.11 | 0.10 | 0.14 | 0.22 | 0.20 | 0.27 | 0.62 | 0.58 | 0.77 | 1.24 | 1.16 | 1.54 |
| **3** | 0.08 | 0.08 | 0.10 | 0.16 | 0.15 | 0.20 | 0.46 | 0.43 | 0.57 | 0.92 | 0.86 | 1.14 |

Notes: Basis of calculations shown in reference 6

Reference 6 provides the basis for the size calculations and can be used for sizing lagoons with various depths at other locations. Appendix A provides climate conditions for various locations in Afghanistan. Aeration system shall be designed for the maximum summer temperatures at the altitude of the project region.

Aeration requirements partial-mix lagoons can be met by floating mechanical aerators. The key to successful aeration is to meet the oxygen demand of the wastewater and to apply the aeration in the upper portion allowing the lower portion to remain quiescent to enhance sedimentation and anaerobic decomposition.

The oxygen transfer rate at standard temperature (20o C) and one atmosphere pressure can be calculated from the following equation

SOTR = AOTR/[(beta\*CsTH-CL)/Cs20)]\*(1.024

^(T-20)

)\*alpha Eq. 3

Where AOTR = actual oxygen transfer rate required under field conditions, kg/h SOTR = standard oxygen transfer rate at 20o C standard conditions, kg/h beta = salinity-surface tension correction factor, assumed = 0.95

CsTH = dissolved oxygen saturation concentration in clean water at temperature T

and altitude H

CL = operating dissolved oxygen concentration, typically 2 mg/L

o

CS20 = dissolved oxygen saturation concentration in clean water at 20

Appendix B

T = wastewater temperature, o C H = altitude, meter

C shown in

alpha = oxygen transfer correction factor for wastewater, typically 0.6 (unit-less)

Mechanical aeration shall be designed for the average high summer temperature and the project site altitude. Appendix A provides outside climate conditions and altitude information at various locations in Afghanistan. Higher temperatures and altitudes increase the mechanical energy required for oxygen transfer because of the lower oxygen solubility at higher temperature and lower oxygen content of less dense air (at higher altitudes). Table 10 presents three examples of the type of information required for aerated lagoon design submittals.

**Table 10. Partial-Mix Aerated Lagoon Aeration Requirements**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Field condition - project** | | **Kandahar** | **Kunduz** | **Kabul** |
| el eva ti on, m | | 1010 | 432 | 1790 |
| el eva ti on, ft | | 3314 | 1417 | 5876 |
| s ummer hi gh, o C | | 41 | 39 | 34 |
| s ummer hi gh, o F | | 106 | 102 | 93 |
| AOTR, kg/da y | | 730 | 720 | 760 |
| SOTR, kg/da y | | 2200 | 2000 | 2260 |
| tota l a era tor, kw | | 48 | 43 | 49 |
|  | CsTH, mg/l | 5.7 | 6.2 | 5.6 |

Mechanical aerators are rated in terms of their standard oxygen transfer rate (SOTR) at standard conditions of temperature and pressure. This rate shall be estimated by using Eq.3 adjusting the AOTR for field conditions at the project site.

**8. System Submittals**

All of the information about the design process and plant selection should be included within the design for review by USACE-AED. Package WWTP shop submittals by the contractor shall include the following:

1. Wastewater treatment plant site plan. The plan shall identify required setbacks, buried utilities (other than sewer) and potential points of connection to the existing electrical distribution system (existing on the compound). The set back requirements for the wastewater treatment plant site shown on a drawing to identify the buildable footprint. Setback requirements shall be obtained from applicable technical criteria listed in Section

01015.

2. Prepare a summary of basis of design report to include the following

Design average daily loading for the wastewater treatment plant based on the design

equivalent population (See Section 01010) to be used as the basis for wastewater loading. Provide the design peak hourly flow rates for the lift station and head works of the plant. The anticipated waste loading in terms of biochemical oxygen demand (BOD5) and total suspended solids (TSS) loading shall be shown for the plant based on wastewater characteristics in the Section 01015.

3. Prepare a treatment train diagram that includes process modules: lift station pumping and flow metering, headwork processes (e.g. grit, trash and scum removal), equalization chamber, primary treatment processes (e.g. sedimentation and aeration), secondary treatment process including aeration and secondary clarification, sludge and scum recirculation systems, effluent chlorination and outfall system, sludge holding/digestion and disposal. All process component tankage shall be above ground steel tank. The biological treatment process shall be activated sludge with extended aeration. The general dimensions of each module shall be specified based on the design capacity requirements of each module shall be shown. The lift station pumps, wet well, hatches, and pump controls, inlet bar screen, distribution weirs and pipe sizes, pump capacity and power requirements, the aeration equipment (diffusers, piping, and blower), and froth control equipment requirements shall be stated. Actual oxygen transfer rates used in the sizing of aeration equipment based on site elevation and high summer temperature range shall be shown. Return ratio ranges for sludge recirculation shall be estimated. Provide pipe and pump capacities on sludge recycling and wasting and calculated sludge storage and disposal volumes required. Show all emergency bypass piping and valve locations.

4. Provide catalogue information for the proposed lift station and treatment plant equipment.

Include information on manufactured steel tanks. Information shall include material standards for field welding of tanks, piping, valves, pumps, pump control equipment, bolts, gaskets, electrical enclosures, central systems control panels, motors and generators, aerators, air piping, blowers, bar screens, handrails, access ladders and service walkway gratings. Provide an access ladder anti-climb gate a minimum of 4 feet above the ladder base to secure the plan from unauthorized entry. Include product coating and lining, and cathodic protection specifications for applicable equipment.

5. Electrical feeds to the waste water treatment plant shall be sized to limit the voltage drop to a total of 5% from the separately derived electrical system to the piece of equipment that is being powered. All breakers, cables and equipment shall be installed and sized in accordance with the latest edition of the National Electrical Code. A layout plan of all the electrical equipment that includes location of the motor control centers, pumps, panels and grounding shall be submitted. The contractors shall also submit panel schedules, motor control center (MCC) layout (with MCC equipment sizes), cable sizes, and electrical equipment sizes and ratings. The contractor shall provide all calculations to show how the equipment was sized.

6. An evaluation of the sludge disposal options and recommendation of the preferred disposal option. The proposed sludge disposal equipment/process requirements shall be shown on a plan drawing.

7. Complete the checklist shown in Table 11 summarizing design parameters, and reference to the drawings where the features are shown. Clearly show dimensions and

numbers of each component.

**Table 11. Summary of WWTP Design Parameters to be Included in Submittal**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Parameter** | **Design**  **Value** | **Units** | **Source or Equation1**  **(with supporting calculations shown)** | **Construction**  **Drawing and Catalogue Reference Number** |
| Average daily flow (ADF) |  | m3/d |  |  |
| Peak hour flow (PHF) |  | m3/hr |  |  |
| Equalization storage volume  7 |  | m3 |  |  |
| Biological loading (BOD5) 2 |  | kg BOD5 /day |  |  |
| Primary Reactor Volumetric  organic loading rate, Lorganic |  | kg/ BOD5 /103 m3 –day  3 |  |  |
| Mixed Liquor Suspended  Solids (MLSS) |  | mg/L |  |  |
| Food:Microorganism Mass  (FM) ratio |  | kg BOD5 /MLVSS-day |  |  |
| Site conditions; high and  low temperature range;  altitude (see section 01015) |  |  |  |  |
| Mechanical aerator or differ  system actual oxygen transfer rate (AOTR) under field conditions temperature and atmospheric pressure (altitude) at project site |  | kg O2 /h |  |  |
| Standard oxygen transfer  rate (SOTR) under standard pressure and temperature conditions per manufacturer4 |  | kg O2 /h |  |  |
| Number and power  requirements of each aerator or diffuser blower system for each treatment  unit (indicate standby units) |  | kW/number |  |  |
| Estimate of annual energy  required based on ADF |  | kWh |  |  |
| Secondary clarifier overflow  rate |  | m3/ m2 -day |  |  |
| Disinfection chamber  volumetric hydraulic residence time |  | minutes 5 |  |  |
| Sludge storage volume |  | m3 |  |  |
| Sludge drying bed loading  rate (if applicable) |  | m2/person-month 6 |  |  |
| Effluent channel peak flow  capacity |  | m3/sec |  |  |
| Panel schedules, motor  control center (MCC) layout (with MCC equipment sizes), cable sizes, and electrical equipment sizes and ratings |  | varies |  |  |

Notes: 1. Documentation for sources shall cite name and date of standard, data collection, or if an equation, all parameter symbols shall be defined used in the equation

2. if process provides nitrogenous oxygen demand removal, include this loading

3. if other basis for reactor sizing is used such as mean cell residence time or F/M ratio provide, appropriate units

4. provide documentation from equipment manufacturer of aerator or diffuser system

5. minimum 30 minute contact time

6. only open beds are permitted

7. Equalization storage shall be adequate for flow variation over 24-hour period as shown in Appendix C

The lagoon system submittals shall include the additional following information in addition to Table 11 data:

1. Liner or impervious layer design for the pond including plan and elevation drawings showing liner/layer thickness, anchoring for synthetic line, side slope, liner/layer bedding preparation, pond cover layer protection, access route for equipment entry into pond for maintenance, synthetic layer specifications and details of pipe penetrations through liner/layer.

2. Mechanical aeration equipment design and specifications.

3. Size of conveyance channel or pipes and invert elevations at each pond.

All submittals shall include the WWTP proposed start-up testing and training program in including operation and maintenance manuals. When the wastewater system construction nears completion and all units are operative, the contractor shall commence a commissioning and startup procedure for the treatment system. The treatment system includes all lift stations, force main, gravity sewers, treatment plant units and associated equipment, sludge holding and digestion, septage dump pad, and laboratory building. The contractor will operate the treatment facility for a trial period of two months performing all daily and weekly operation and maintenance (O&M) tasks recommended by the equipment manufacturer. The contractor shall utilize services of qualified operators; including the use of at least two Afghan Nationals that the contractor shall train. During the routine O&M, the contractor shall perform all sampling and testing necessary to ensure proper daily operations in achieving the required effluent standards. The contractor shall maintain a log that includes records of daily O&M activities, e.g. repairs, inflow measurement, aeration cycles, effluent cycling, waste and return sludge pumping, and sludge drying. The contractor shall also maintain and operate the sludge disposal operation during the trial period.

Project submittal shall include markup UFGS specification 44 41 13 Prefabricated Biochemical Wastewater Treatment Plant. The specification paragraph 1.2.1 “Extended Aeration Plant Design” shall be changed to Activated Sludge Plant Design Type [extended aeration], [contact stabilization], [sequencing batch reactor]”. Strike out the inapplicable type. Appendix D contains a list of the specific strike-out topics to be edited by the designer.

**9. As-Builts**

Upon completion of installing the package wastewater treatment plant, the contractor shall submit editable CAD format As-Built drawings. The drawing shall show the final product as it was installed in the field, with the exact dimensions, locations, materials used and any other changes made to the original drawings. Refer to Contract Sections 01335 and 01780A of the specific project for additional details.

**10. References**

1. Overseas Environmental Baseline Guidance Document, Department of Defense, 2007

2. Standard Methods for the Examination of Water and Wastewater, American Public Health

Association (APHA) publication, current edition.

3. UFC 3-240-09FA Domestic Wastewater Treatment, 2004

4. Small and Decentralized Wastewater Management Systems, Crites and Tchobanoglous, Metcalf & Eddy, McGraw- Hill, 1998

5. Wastewater Engineering Treatment and Reuse, Metcalf & Eddy, McGraw- Hill, 2003

6. US EPA. Municipal Wastewater Stabilization Ponds – Design Manual, EPA-625/1-83-015,


1983

7. Report of the Wastewater Committee of the Great Lakes – Upper Mississippi River Board of State and Provincial Public Health and Environmental Managers. Ten State Standards for Wastewater Facilities. 2004

**Appendix A - Outside Design Climate Conditions**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Bagram Area** |  |  | **Darualaman Area** |  |
|  |  |  |  |  |
| **Latitude:** | 35.0 deg North |  | **Latitude:** | 34.42 deg North |
| **Longitude:** | 69.0 deg East |  | **Longitude:** | 69.11 deg East |
| **Elevation:** | 1490 M (4888 Ft) |  | **Elevation:** | 1737 M (5700 Ft) |
| **Summer Temp:** | DB: 35o C (95o F) |  | **Summer Temp:** | DB: 34o C (93o F) |
|  | WB: 18.6 oC (66 oF) |  |  | WB: 15.6 oC (60 oF) |
| **Winter Temp:** | -12.8 oC (9 oF) |  | **Winter Temp:** | -8 oC (18 oF) |
| **Daily Range:** | 18.3 oC (33 oF) |  | **Daily Range:** | 8 oC (15 oF) |
|  |  |  |  |  |
|  |  |  |  |  |
| **Farah Area** |  |  | **Gardez Area** |  |
|  |  |  |  |  |
| **Latitude:** | 32.22 deg North |  | **Latitude:** | 33.6 deg North |
| **Longitude:** | 62.11 deg East |  | **Longitude:** | 69.22 deg East |
| **Elevation:** | 700 M (2297 Ft) |  | **Elevation:** | 1737 M (7710 Ft) |
| **Summer Temp:** | DB: 41.1o C (106o F) |  | **Summer Temp:** | DB: 29o C (84o F) |
|  | WB: 22.5 oC (72.5 oF) |  |  | WB: 12.2 oC (54 oF) |
| **Winter Temp:** | 1.6 oC (35 oF) |  | **Winter Temp:** | -10 oC (14 oF) |
| **Daily Range:** | unknown |  | **Daily Range:** | unknown |
|  |  |  |  |  |
|  |  |  |  |  |
| **Ghanzni/Khair Kot**  **Area** |  |  | **Herat Area** |  |
|  |  |  |  |  |
| **Latitude:** | 33 deg North |  | **Latitude:** | 34.22deg North |
| **Longitude:** | 68 deg East |  | **Longitude:** | 62.22 deg East |
| **Elevation:** | 2183 M (7162 Ft) |  | **Elevation:** | 964 M (3163 Ft) |
| **Summer Temp:** | DB: 30.5o C (87o F) |  | **Summer Temp:** | DB: 38o C (100o F) |
|  | WB: 15.6 oC (60 oF) |  |  | WB: 20 oC (68 oF) |
| **Winter Temp:** | -7.2 oC (19 oF) |  | **Winter Temp:** | -6 oC (21 oF) |
| **Daily Range:** | unknown |  | **Daily Range:** | 9 oC (17 oF) |
|  |  |  |  |  |
|  |  |  |  |  |
| **Jalalabad Area** |  |  | **Kabul Area** |  |
|  |  |  |  |  |
| **Latitude:** | 34 deg North |  | **Latitude:** | 34.31deg North |
| **Longitude:** | 70 deg East |  | **Longitude:** | 69.12 deg East |
| **Elevation:** | 580 M (1903 Ft) |  | **Elevation:** | 1800 M (5900 Ft) |
| **Summer Temp:** | DB: 39.6o C (103o F) |  | **Summer Temp:** | DB: 19o C (68o F) |
|  | WB: 25.6 oC (78 oF) |  |  |  |
| **Winter Temp:** | 4.6 oC (40 oF) |  | **Winter Temp:** | -5 oC (42 oF) |
| **Daily Range:** | unknown |  | **Daily Range:** | 11 oC (20 oF) |

**Appendix B - Solubility of Oxygen in Fresh Water**



EQUALIZATION BA SIN STORAGE VOLUME

Hyd ra ulic loading

255,588 Uday

255.6 cu m/day

0.003 cum m/sec

)('

**n**



**Average**

**flow rate Cumulativ ADF**

300 .-.-,-,-,-.-.--.-r-r-r-r-r-r-r-.-.-.-.-.-. r-r-r-r-r-r-r-.-o **c**

**!a**

ADF

0.895

0.716

0.537

**Interval**

1

2

3

**Period**

**M-1**

1-2

2-3

**m/sec**

0.003

0.002

0.002

**period! m m**

10 11

17 21

23 32

250 I

I I I

I I I I

I I I

I I I I I

I I I

I I I

I.,**U** I

I I I I I

§

**s·**

**a**

**o· i'ii**

**0**

0.342 5

0.325 6

4-5

0.001

0.001

31 53

34 64

i-::l

llll l

llll l lllRIIIII I IIII I

**:I**

**9,** ;;?

-

-.I

0.667 8

1.155 9

1.334 10

1.383 11

1.399 12

7-8

8-9

9-10

10-11

11-N

0.002

0.003

0.004

0.004

0.004

46 85

58 96

72 106

87 117

102 128

1.Ill 1ao I

=

I I I

I I I

I I **"T l A** I I I

I I I

I I I I

I I I

I I I I I

**e!.**

**;::j'**

**ao·**

**:I**

**<C:;o**

**"IJ..O**

**am**

**3**

1.318 14

1.139 16

1.058 17

1.058 18

1.074 19

1.302 21

1-2

3-4

4-5

6-7

8-9

0.004

0.003

0.003

0.003

0.003

0.004

131 149

158 170

167 181

179 192

190 202

217 224

*a* I I I I

**loP**

0

I **U1 I J/r** I I I:J':t c

....

t : uaizaioA'

**tD**

**0**..,**'**

**i**

Ill

1.188 20

1.302 22

1.237 23

7-8

9-10

10-11

0.004

0.004

0.004

203 213

230 234

244 245

0 5 10

15 20 25 30

**Time Period,. hours**

**cal**

1.123 24

11-M

0.003

258 258

**-11- Cumulative volume at end of period, m3**

**.........\_AOF Cumulative Volume, m3**

**Average daily flow from design above 0.003**

**;i**

**Appendix D – Summary of Markup Pages for UFGS 44 41 13 – Prefabricated Biochemical**

**Wastewater Treatment Plant**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Topic | Page | Edit Options | Comments | References |
|  |  |  |  |  |
| Paragraph 1.2.1 Extended  Aeration | 4 | “Extended Aeration  Plant Design” shall be changed to Activated Sludge Plant” |  |  |
| Paragraph 1.2.1 Activated  Sludge Plant | 4 | Insert Select Design  Type: [extended aeration], [contact stabilization], [sequencing batch reactor] – strike others |  | USACE –AED Package  Wastewater Treatment Plant Design Requirements, 2009 |
| Paragraph 1.2.1 Activated  Sludge Plant | 5 | Insert design and peak  flow rates for plant  (L/day) in brackets | Select peak flow as 2.5  times average day flow | UFC 3 240-09fa |
| Paragraph 1.2.1 Activated  Sludge Plant | 5 | Insert 400 mg/L for  BOD5 and 400 mg/L for TSS; Insert 92.5 % for removal |  | Effluent standards shall  meet requirements in “Overseas Environmental Baseline Guidance Document”, Department of Defense, 2007 |
| Paragraph 1.2.1 Activated  Sludge Plant | 5 | Strike last sentence in  paragraph concerning seismic design |  |  |
| Paragraph 1.2.1.1 Aeration  Zone | 5 | Insert minimum  wastewater depth and freeboard; insert influent pipe diameter |  |  |
| Paragraph 1.2.1.2 Sludge  Settling Zone | 5-6 | Insert surface loading  rate at average daily flow rate and surface loading rate at peak hourly flow rate; edit scum baffle height |  |  |
| Paragraph 1.2.1.3 Sludge  Holding Zone | 6 | Insert sludge holding  capacity |  |  |
| Paragraph 1.2.1.4  Chlorination Zone |  | Insert chlorination zone  effluent pipe diameter |  |  |
| Paragraph 1.2.2 | 6-8 | Delete in entirety |  |  |
| Paragraph 1.3 Submittals | 8 | Insert USACE-AED-EC  in bracket after “G” |  |  |
| Paragraph 1.6 Extra  Materials | 10 | Insert one month in  bracket |  |  |
| Paragraph 2.4 Sewage  Shredder | 13 | Indicate zone; add  batch reactor plant |  |  |
| Paragraph 2.4.3 Sewage  Shredder Motor and mounting | 14 | Insert motor voltage, phase and change 60  to 50 Hz |  |  |
| Paragraph 2.5.1 Blower  Capacity | 14 | Inset blower capacity  SCFM and pressure kPA |  |  |
| Paragraph 2.5.2 Blower  Drive | 15 | Insert blower, rpm,  motor voltage and phase; revise 60 to 50  Hz |  |  |
| Paragraph 2.5.5 Blower  Drive | 15 | Insert pressure relief  valve set-point pressure |  |  |

Notes: 1. Other than deletions/edits shown in this table the standard specification 44 41 13 shall be retained in its entirety

**Appendix D – Summary of Markup Pages for UFGS 44 41 13 – Prefabricated Biochemical**

**Wastewater Treatment Plant (Continued)**

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Topic | Page | Edit Options | Comments | References |
|  |  |  |  |  |
| Paragraph 2.6.1 Air  Diffusion Performance and  Design requirements | 16 | Insert 3 cubic meters of air per 100 cubic  meters of tank volume |  |  |
| Paragraph 2.6.2 Air  Diffusion Piping and Valves | 16 | Select piping material  and state number of separate diffusers per tank |  |  |
| Paragraph 2.7.1 Sludge and  Scum Piping and Valves | 17 | Select zone for sludge recirculation; for batch  reactor indicate sludge storage |  |  |
| Paragraph 2.7.2 Sludge and  Scum Air lift Pumps | 17 | Insert sludge draw or  recirculation percent;  add frequency |  |  |
| Paragraph 2.9.1 Gas  Chlorinator | 19-20 | Delete paragraph and all subparagraphs | Use calcium hypochlorite solution  chlorinator, paragraph  2.10 |  |
| 17Paragraph 2.10.2  Calcium Hypochlorite Chlorination System Metering Pump | 21 | Select type of metering  pump, motor enclosure, motor voltage, phase, and change 60 to 50 Hz |  |  |
| Paragraph 2.11 Sewage  Pumps | 22 | Select final effluent as  required |  |  |
| Paragraph 2.11.1 Sewage  Pumps | 22 | Select motor enclosure |  |  |
| Paragraph 2.12 Flow meter  and Control | 22-23 | Delete all but one  applicable paragraph leaving one paragraph as flow metering  method |  |  |
| Paragraph 3.5.2 Welding | 25-26 | Delete paragraph and  subparagraphs |  |  |
| Paragraph 8 Field training | 27 | Insert hours of training | As per contract  technical requirements or minimum per manufacturer’s  recommendation;  whichever greater |  |

Notes: 1. Other than deletions/edits shown in this table the standard specification 44 41 13 shall be retained in its entirety