## Appendix B
Water Well Construction Flow Chart
Preliminary Well Development |  | Production Well Development |  | Well Pump and Wellhead Completion
1 | Pre Construction Meeting | 10 | Well Installation | 19 | **Submittal** Pump Selection Approval
2 | Site Preparation | 11 | Install Screen and Final Casing | 20 | Final Well Pump and Discharge Piping Installation
3 | Surface Casing Installation | 12 | Install Gravel Pack, Bentonite Seal and Surface Grout Seal | 21 | Install pump Water Level Sensor, Piping, etc
4 | Pilot Test Hole Drilling | 13 | Well Development | 22 | Disinfect Well
5 | Geologic Logging | 14 | Swab and Airlift | 23 | Well Head Completion Including Building
6 | Groundwater Sampling | 15 | Pump Performance and Sand Tests | 24 | ***Submit*** Well Completion Report
7 | Conslutant Determines Well Design | 16 | Well Completion and Testing | 24 | ***Submit*** Contents of previous Submittals
8 | ** Submittal** Well Design | 17 | Aquifer Test Using Test Pump | 26 | ***Submit*** Pump Equipment and Other material and Product Warranties
9 | Contractor Reams Pilot Borehole to Final Diameter | 18 | Analyze Pump Test Data and Calculate Pump duty Point (TDH, Q)

## Table 2
Table 2. Minimum Distances from Pollution Sources.
Source | Minimum Horizontal Distance
Building Sewer | 15 m ( 50 ft )
Disposal Field / Septic Tank | 30 m ( 100 ft )
Seepage Pit | 30 m ( 100 ft )
Dry Well , Abandoned Well | 15 m ( 50 ft )
Cesspool / Leaching Pits | 45 m (150 ft )
Note: the above minimum horizontal distances apply to wells at all depths. Greater distances are recommended when feasible.

## Table 3
Anticipated Well Yeild | Nominal Size of Pump Bowls | Optimum Size of Well Casing | Smallest Size Well Casing
(lpm) | (mm) | (mm) | (mm)
<380 | 100 | 150 ID | 125 ID
285-660 | 125 | 200 ID | 150 ID
570-1515 | 150 | 250 ID | 200 ID
1325-2460 | 200 | 300 ID | 250 ID
2270-3400 | 250 | 350 OD | 300 ID
3200-4900 | 300 | 400 OD | 350 OD
4550-6800 | 350 | 500 OD | 400 OD
6050-11400 | 400 | 600 OD | 500 OD
(gpm) | (in) | (in) | (in)
<100 | 4 | 6 ID | 5 ID
75-175 | 5 | 8 ID | 6 ID
150-400 | 6 | 10 ID | 8 ID
350-650 | 8 | 12 ID | 10 ID
600-900 | 10 | 14 OD | 12 ID
850-1300 | 12 | 16 OD | 14 OD
1200-1800 | 14 | 20 OD | 16 OD
1600-3000 | 16 | 24 OD | 20 OD
3000-6000 | 20 | 30 OD | 24 OD

## Table 5
Table 5. Minimum PVC SCH 80 Pipe Casing Wall Thicknesses
Casing Diameter |  | Wall Thickness
(mm) | (in) | (mm) | (in)
150 | 6 | 11 | 0.43
200 | 8 | 13 | 0.5
250 | 10 | 15 | 0.59
Note: AED does not allow the use of PVC casing in wells deeper than 80 meters.